## Continuous Slab
Input Quantities
Dimensions |  |  | Material Properties
Slab Length (m) | 5.8 |  | Concrete Compressive Strength (kn)/m^2 | 30000
Slab Width (m) | 1 |  | Steel Yield Strength (kn)/m^2 | 500000
Slab Depth (m) | 0.175 |  | Unmodified SLS Stress (kn/m^2) | 242000
Wall Thickness (m) | 0.2 |  | Rebar Diameter (m) | 0.012
Environmental Cover | 0.015 |  | Bar Links (m) | 0.008
Deviation Allowance | 0.01 |  | Concrete Density (kn/m^3) | 25
Chord Width (depth + 2 * ( rebar cover + bar links + rebar diameter/2)*slope | 0.1828 |  | Screed Density (kn/m^3) | 20
Loading
Permanent Load | Slab | Screed | Finishes | Services |  | Variable Load
Depth (m) | 0.175 | 0.05 | 0 | 0 |  | Live Load | 2.5
Width (m) | 1 | 1 | 0 | 0 |  | Partition Load | 0.8
Density (kn/m^3) | 25 | 20 | 0 | 0
Code Loading (kn/m^2) | 0 | 0 | 0.5 | 0 |  | Total Permanet Load | 5.875
Total Load (kn/m^2) | 4.375 | 1 | 0.5 | 0 |  | Total Variable Load | 3.3
Ultimate Loading (either 6.10 or worst of 6.10a and 6.10b)
Note that the phi values in each equation must be added (I'll add in table)
If there are additional load patterns (such as wind loads or roof loads, they are multiplied by the phi values)
EN 6.10 | 12.8812
EN 6.10A | 11.3963
EN 6.10B | 12.2937
Load | 12.2937
Phi values | Residential | Office | Congregation | Shopping | Storage | Traffic | Parking | Roofs | Snow | Wind | Fire
| 0.7 | 0.7 | 0.7 | 0.7 | 1 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.6
Nominal Cover = max(bar diameter, environmental conditions) + cover deviation allowance | 0.025
a1 (end allowance) | 0.0875
a2 (end allowance) | 0.0875
Effective Span (l_eff) | 5.975
Effective Depth = thickness - nominal cover - bar diameter/2 | 0.144
Design Moment
M_end = EN6.10 * C2 Coefficient for one-way slab * Effective span^2 | 37.7449
M_internal = EN6.10 * C2 Coefficient for one-way slab * Effective span^2 | 27.6504
V_ext = Coefficient * Load * Effective Span | 29.3821
V_support | 44.0731
Flexural Design (External Spans) |  |  | Flexural Design (internal spans)
Deflection K = moment/width*effective depth^2*cylinder strength | 0.060675
z = effective depth/2 * (1+(1-3.53*K)^0.5 | 0.13583
Required Reinforcement Area = M_ed / z * reinforcement yield strength | 0.00063915 |  | Required Reinforcement Area = M_ed / z * reinforcement yield strength | 0.00046822
Trying Allowable Reinforcement | 0.000645 |  | Trying Allowable Reinforcement | 0.000502
rho = A_s/A_c = A_s/(b_w*d_eff+ (b_eff-b_w)h_f) = Area/(width between tension and compression chords*effective depth + (width-chord width) * 100) | 0.0044386 | << not a percentage, would be 100 times higher if percent | rho = A_s/A_c = A_s/(b_w*d_eff+ (b_eff-b_w)h_f) = Area/(width between tension and compression chords*effective depth + (width-chord width) * 100) | 0.0032515
rho_0 = f_ck^0.5 | 0.0054772
Deflection
End Span | [5 empty] | Internal Span
N span/depth = 11+1.5sqrt(f_ck)*p_o/rho + 3.2sqrt(f_ck)(rho_o/rho - 1)^1.5 | K (from 7.4N) | F1 (beff/bw) | F2 | F3 |  | N span/depth = 11+1.5sqrt(f_ck)*p_o/rho + 3.2sqrt(f_ck)(rho_o/rho - 1)^1.5 | K (from 7.4N) | F1 (beff/bw) | F2 | F3
23.1224 | 1.3 | 1 | 1 | 1.1931 |  | 34.766 | 1.5 | 1 | 1 | 1.3291
|  | ^^ 1 since no beams or flanges | ^^ span < 7m |  |  |  |  | ^^ 1 since no beams or flanges | ^^ span < 7m
Span-depth — found in table (lightly stressed) | True L/d | Allowable L/d = N * K * F1 * F2 * F3 | Stress (sigma_s = f_yk/gamma_s * A_sreq/A_sprov) * ((dl+0.3*ll) / total load) * 1.08 | Max Span |  | Span-depth — found in table (lightly stressed) | True L/d | Allowable L/d = N * K * F1 * F2 * F3 | Stress (sigma_s = f_yk/gamma_s * A_sreq/A_sprov) * ((dl+0.3*ll) / total load) * 1.08 | Max Span
20 | 33.1429 | 35.8625 | 259835.3018 | 5.1642 |  | 20 | 33.1429 | 69.3103 | 233243.5914 | 9.9807
Increased Reinforcement | 0.000754
N span/depth = 11+1.5sqrt(f_ck)*p_o/rho + 3.2sqrt(f_ck)(rho_o/rho - 1)^1.5 | K (from 7.4N) | F1 (beff/bw) | F2 | F3
23.1224 | 1.3 | 1 | 1 | 1.3947
|  | ^^ 1 since no beams or flanges | ^^ span < 7m
Span-depth — found in table (lightly stressed) | True L/d | Allowable L/d = N * K * F1 * F2 * F3 | Stress (sigma_s = f_yk/gamma_s * A_sreq/A_sprov) * ((dl+0.3*ll) / total load) * 1.08 | Max Span
20 | 33.1429 | 41.923 | 222272.9041 | 6.0369
Allowable/Actual | Actual/Allowable | Allowable?
0.89038 | 1.1231 | TRUE
Shear
k-factor | 2
V_ed | 26.5361
V_ed interior | 41.2271
V_rdc | 68.2271
V_rdcmin | 78.0793
Allowable? | TRUE